## Slide 1
The recording and slides of this webinar will be made available to attendees via email within later today
PDH Certificates will be e-mailed to attendees within 2 days.
Precise Cooling Temperature Control Ensures Quality and Increased Cycle Counts
Bert Wesley, P.E., Woodard & Curran
Keynote Speaker

## Slide 2: Q&A Format
Panelists will answer your questions during the Q&A session at the end of the Webinar.
Please post your questions in the Questions Window in your GoToWebinar interface.
Direct all questions to Chiller & Cooling Best Practices® Magazine

## Slide 3: Handouts

## Slide 4: Disclaimer
All rights are reserved. The contents of this publication may not be reproduced in whole or in part without consent of Smith Onandia Communications LLC. Smith Onandia Communications LLC does not assume and hereby disclaims any liability to any person for any loss or damage caused by errors or omissions in the material contained herein, regardless of whether such errors result from negligence, accident, or any other cause whatsoever.
All materials presented are educational. Each system is unique and must be evaluated on its own merits.

## Slide 6
Introduction
Chiller & Cooling Best Practices® Magazine
Precise Cooling Temperature Control Ensures Quality and Increased Cycle Counts

## Slide 7: About the Speaker
Sr. Principal, Industrial Plant Engineering Practice Leader Woodard & Curran
30 years in heavy industry
Deliver utility applications tailored to manufacturing equipment
Bert Wesley, P.E.
Woodard & Curran

## Slide 8: Presentation Particulars
Discussion today will use general numbers that are close but not exact for ease of discussion
Not an advertisement for any product or service
Many ways to accomplish the goal
  Keep open mind
  Some items were changed at the request of the client

## Slide 9: Client – rPlanet Earth, Vernon, CA

## Slide 10: High Speed Manufacturing Equipment has Exacting Requirements
How do we design for multiple users and varying requirements?
Single looped system for all users
Maintain loop pressure
5 Injection Molders
7 Sheet Lines
2 Thermoformers

## Slide 11: Design Considerations – Chilled Water
Injection Molder 345 GPM at 45 psi
Sheet Line 254 GPM at 52 psi
Thermoformer 123 GPM at 55 psi
If these conditions are not met, the equipment can fault out
Three design points:
Zero – what happens when there’s no call for cooling water
Steady state – Normal operation of the equipment
Infinity – All production lines call for cooling water simultaneously

## Slide 12: Sheet Extrusion Line

## Slide 13: Thermoformer

## Slide 14: Chiller Plant Design – Old ways
Primary/ Secondary
Many Pumps – constant fluid circulation regardless of process load
Hot tank/Cold tank – buffer capacity – large volume 20,000 gallons each
Large capital investment
Large footprint
Large energy demand not necessarily tied to production schedule
Definitely works. Can we do it more efficiently?

## Slide 15: Chiller Plant Design Newer
Variable Primary (Variable Speed Pump)
Recirculation valves to keep the header at target temperature
Combination hot/cold tank
Much lower volume due to lack of space for the tank(s)

## Slide 16: Husky Injection Molder

## Slide 17: Simple System Schematic

## Slide 18: Chilled Water Equipment
Model: CVHF0570
Capacity: 600 Tons
Centrifugal water-cooled chiller has two shell-and-tube heat exchangers; the evaporator (low pressure) and condenser (high pressure) sides and a compressor
Centrifugal Chiller

## Slide 19: Chiller P&ID

## Slide 20: Hot/Cold Tank 2500 Gal

## Slide 21: Design Innovation
Added flow meter to the chilled water supply line to manufacturing
Added flow meter to the tank bypass line
Numerous temperature transmitters throughout the piping network
  Solenoids open to allow chilled water flow as temperature in the supply pipe warms up

## Slide 22: Enhanced Flow Management Package
Trane Chiller Enhanced Flow Management Package
Uses a variable water-flow compensation algorithm
Published data claims temperature control at a change in water flow rate of 30% per minute
Field actual performance controls temperature to water flow rate of 50% per minute
Any additional water the chiller can chill is routed to the hot/cold tank via the control valve
As flow rate increases to the production equipment, the chiller can chill more water than the production equipment requires (in most scenarios), and the residual water is diverted back to the hot tank, to prechill the incoming hot water from the production equipment.

## Slide 23: Flow Change with EFMP

## Slide 24: Flow Change without EFMP

## Slide 25: Innovation Solutions
Calculated using several flow model software packages
Design collaboration with Trane Chiller Design Engineers
  Trip to La Crosse, WI for design application meeting

## Slide 26: Quick Reference Screen

## Slide 27: Chiller & Tank Control Screen

## Slide 28: Results
Production machine cycle time lowered from 17 seconds per cycle to 13 seconds per cycle.
30% Increase in Production!!!
211 cycles/hour * 100 preforms = 210,000 preforms (at 17 seconds)
276 cycles/hour * 100 preforms = 276,000 preforms (at 13 seconds)

## Slide 29: Machine Cycle

## Slide 30: Key Learnings
Exact Temperature Control is possible given today’s components
Many decisions are needed to ensure optimal success
Embrace new ideas and techniques after proper vetting

## Slide 31
Please submit any questions through the Question Window on your GoToWebinar interface, directing them to Chiller & Cooling Best Practices Magazine. Our panelists will do their best to address your questions and will follow up with you on anything that goes unanswered during this session.
Thank you for attending!
Q&A
Precise Cooling Temperature Control Ensures Quality and Increased Cycle Counts

## Slide 32: Thank you for attending!
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to Attendees within 2 days.

## Slide 33
Thursday, December 16, 2021 – 2:00 PM EST
Register for free at
www.airbestpractices.com/magazine/webinars
December 2021 Webinar Measuring KPI’s for Efficiency: kW, Flow and Pressure
Sponsored by
Tim Dugan
Compression Engineering Corporation
Keynote Speaker